## Sheet1
AssetID | AssetType | FunctionalLocation | Component_ID | Component information_added | ISO14224 Equipment Class_added | ISO14224 Equipment ClassDescription_added | ISO14224_FailureModeCode_added | ISO14224_FailureModeDescription_added | ISO14224_FailureMechanismCategory_added | ISO14224_FailureMechanismSubdivision_added | Company_Functional_Purpose | Company_FailureMode don't add | Company_FailureMechanism don't add | HiddenFailure | Company_FailureEffect | MaintenanceStrategy | ControlMeasure | ControlFrequency | ControlGroup don't add
ACX1 |  | Loop 02767 | LSH02767 | Radiation level sensor |  |  |  |  | Instrument failure | Out of adjustment | Detect clave high level | Not switching | Misalignment | Y | Overfilling during charge step (insufficient vapour space in clave) results in the H2 pressure control being unable to respond correctly | PM | Shutter Test | 52W | Maint | PSV02014 lifts, release of powder / liquor and vapour to atmosphere at elevated location. Ignition not considered credible (classified hazardous area), vapour will contain steam. Potenital for serious harm for personnel in immediate vicinity of PSV. LOPA 25.18
ACX1 |  | Loop 02767 | LSH02767 | Radiation level sensor |  |  |  |  | Instrument failure | Out of adjustment | Detect clave high level | Not switching | Misalignment | Y | Overfilling during charge step (insufficient vapour space in clave) results in the H2 pressure control being unable to respond correctly | PM | Wipe Test | 52W | Maint | PSV02014 lifts, release of powder / liquor and vapour to atmosphere at elevated location. Ignition not considered credible (classified hazardous area), vapour will contain steam. Potenital for serious harm for personnel in immediate vicinity of PSV. LOPA 25.18
ACX1 |  | Loop 02767 | LSH02767 | Radiation level sensor |  |  | FTF |  | Electrical failure | General - related to supply and transmission of electrical power - no further details | Detect clave high level | Not switching | Hardware failure | Y | Overfilling during charge step (insufficient vapour space in clave) results in the H2 pressure control being unable to respond correctly | PM | Shutter Test | 52W | Maint | PSV02014 lifts, release of powder / liquor and vapour to atmosphere at elevated location. Ignition not considered credible (classified hazardous area), vapour will contain steam. Potenital for serious harm for personnel in immediate vicinity of PSV. LOPA 25.18
ACX1 |  | Loop 02767 | LSH02767 | Radiation level sensor |  |  | FTF |  | Electrical failure | General - related to supply and transmission of electrical power - no further details | Detect clave high level | Not switching | Hardware failure | Y | Overfilling during charge step (insufficient vapour space in clave) results in the H2 pressure control being unable to respond correctly | PM | Wipe Test | 52W | Maint | PSV02014 lifts, release of powder / liquor and vapour to atmosphere at elevated location. Ignition not considered credible (classified hazardous area), vapour will contain steam. Potenital for serious harm for personnel in immediate vicinity of PSV. LOPA 25.18
ACX1 |  | Loop 02766 | TE02766 | Temperature sensor |  |  |  |  | Instrument failure | Faulty signal | Add steam to control clave temperature | Inaccurate reading | Inherent | Y | Potentially overheat the clave | PM | Calibration | 104W | Maint | Prolonged overheating can cause damage to clave
RV01 | Control loop | CL 02766 | TIT02766 | Temperature indicating transmitter | CL | Control logic units | AIR | Abnormal Instrument Air | Instrument failure | Control failure | Add steam to control vessel temperature | Inaccurate reading | Inherent | Y | Potentially overheat the vessel | PM | Calibration | 104W | Maint
RV01 | Control loop | CL 02766 | TV02766 | Temperature control valve | VA | Valves | SPO | Spurious operation | Material failure | Wear | Add steam to control vessel temperature | Erratic/Sticking | Wear | N | Potentially overheat the vessel | PM | Stroke check | 104W | Maint
RV01 | Control loop | CL 02766 | TV02766 | Temperature control valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | Add steam to control vessel temperature | Passing | Wear | Y | Potentially overheat the vessel | PM | OSR | 208W | Maint
ACX1 |  | Loop 02773 | PIT02773 | Pressure indicating transmitter |  |  |  |  | Instrument failure | Faulty signal | Control clave pressure by controlling air vent and H2 inlet control | Inaccurate reading | Inherent | Y | Potential to over pressure the clave | PM | Calibration | 208W | Prod | Clave unsafe to run without pressure measurement
ACX1 |  | Loop 02773 | PIT02773 | Pressure indicating transmitter |  |  | PLU |  | External influence | Blockage/ plugged | Control clave pressure by controlling air vent and H2 inlet control | Tapping blocked | Process conditions | Y | Potential to over pressure the clave | PM | Inspect tappings | 52W | Maint | Error in reading causing erratic pressure control
ACX1 |  | Loop 02773 | PIT02773 | Pressure indicating transmitter |  |  | PLU |  | External influence | Blockage/ plugged | Control clave pressure by controlling air vent and H2 inlet control | Tapping blocked | Process conditions | Y | Potential to over pressure the clave | Spare | Crit spare | As needed | Maint
ACX1 |  | Loop 02774 | PIT02774 | Pressure indicating transmitter |  |  | AIR |  | External influence | Blockage/ plugged | Control clave pressure by controlling air vent and H2 inlet control | Inaccurate reading | Inherent | Y | Potential to over pressure the clave | PM | Calibration | 208W | Prod | Clave unsafe to run without pressure measurement
ACX1 |  | Loop 02774 | PIT02774 | Pressure indicating transmitter |  |  | PLO |  | External influence | Blockage/ plugged | Control clave pressure by controlling air vent and H2 inlet control | Tapping blocked | Process conditions | Y | Potential to over pressure the clave | PM | Inspect tappings | 52W | Maint | Error in reading causing erratic pressure control
ACX1 |  | Loop 02774 | PIT02774 | Pressure indicating transmitter |  |  | PLO |  | External influence | Blockage/ plugged | Control clave pressure by controlling air vent and H2 inlet control | Tapping blocked | Process conditions | Y | Potential to over pressure the clave | Spare | Crit spare | As needed | Maint
RV01 | Control loop | CL 02774 | PV02774-1 | Pressure valve | VA | Valves | FTO | Failure to open on demand | Mechanical failure | Sticking | vessel H2 vent control | Stuck closed | Foreign object | Y | Cannot control pressure in vessel | PM | OSR | 26W | Maint
RV01 | Control loop | CL 02774 | PV02774-1 | Pressure valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | vessel H2 vent control | Passing | Wear | Y | Cannot control pressure in vessel | Spare | Rotable spare | As needed | Maint
RV01 | Control loop | CL 02774 | PV02774-3 | Pressure valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | vessel H2 inlet control | Passing | Wear | Y | Cannot control pressure in vessel | PM | OSR | 208W | Maint
RV01 | Control loop | CL 02774 | PV02774-3 | Pressure valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | vessel H2 inlet control | Passing | Wear | Y | Cannot control pressure in vessel | Spare | Rotable spare | As needed | Maint
ACX1 |  | Loop 02774 | ZI02774-3 | Position indicator |  |  |  |  | Instrument failure | Faulty signal | Clave H2 inlet control | Passing | Wear | Y | Cannot control pressure in Clave | PM | OSR | 208W | Maint | Pressure control becomes unstable. Potential release of process through PSV. Typically throttling. Clean H2. Rare to be stuck closed or open. Will stop at end of cycle.
ACX1 |  | Loop 02774 | ZSC02774-3 | Position switch closed |  |  |  |  | Instrument failure | Faulty signal | Clave H2 inlet control | Passing | Wear | Y | Cannot control pressure in Clave | PM | OSR | 208W | Maint | Pressure control becomes unstable. Potential release of process through PSV. Typically throttling. Clean H2. Rare to be stuck closed or open. Will stop at end of cycle.
RV01 | Control loop | CL 02774 | PV02774-2 | Pressure valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | vessel air vent control | Passing | Wear | Y | Cannot control pressure in vessel | PM | OSR | 208W | Maint
RV01 | Control loop | CL 02774 | PV02774-2 | Pressure valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | vessel air vent control | Passing | Wear | Y | Cannot control pressure in vessel | Spare | Rotable spare | As needed | Maint
RV01 | Control loop | CL 02778 | XV02778 | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel H2 vent block | Passing | Wear | Y | Safety | PM | OSR | 208W | Maint
RV01 | Control loop | CL 02778 | XV02778 | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel H2 vent block | Passing | Wear | Y | Safety | Spare | Rotable spare | As needed | Maint
ACX1 |  | Loop 02778 | ZSO02778 | Position switch open |  |  |  |  | Instrument failure | Faulty signal | Clave H2 vent block | Passing | Wear | Y | Safety | PM | OSR | 208W | Maint | Typically open when in use. Closes when complete. Can have air suction if passing. Safety. Stroked as part of densification
ACX1 |  | Loop 02778 | ZSC02778 | Position switch closed |  |  |  |  | Instrument failure | Faulty signal | Clave H2 vent block | Passing | Wear | Y | Safety | PM | OSR | 208W | Maint | Typically open when in use. Closes when complete. Can have air suction if passing. Safety. Stroked as part of densification
RV01 | Control loop | CL 02777 | XV02777 | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel air vent block | Passing | Wear | Y | Safety | PM | OSR | 208W | Maint
RV01 | Control loop | CL 02777 | XV02777 | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel air vent block | Passing | Wear | Y | Safety | Spare | Rotable spare | As needed | Maint
ACX1 |  | Loop 02777 | ZSO02777 | Actuated on/off valve |  |  |  |  | Instrument failure | Faulty signal | Clave air vent block | Passing | Wear | Y | Safety | PM | OSR | 208W | Maint | Typically open when in use. Closes when complete. Can have air suction if passing. Safety.
ACX1 |  | Loop 02777 | ZSC02777 | Actuated on/off valve |  |  |  |  | Instrument failure | Faulty signal | Clave air vent block | Passing | Wear | Y | Safety | PM | OSR | 208W | Maint | Typically open when in use. Closes when complete. Can have air suction if passing. Safety.
ACX1 |  | Loop 02776 | FIT02776 | Flow indicating transmitter |  |  |  |  | Instrument failure | Faulty signal | Control clave feed air | Inaccurate reading | Inherent | Y | Malfunction of air control loop | PM | Calibration | 104W | Maint | High pressure in clave. LOPA 25.09, 25.10
ACX1 |  | Loop 02776 | FIT02776 | Flow indicating transmitter |  |  | PLU |  | External influence | Blockage/ plugged | Control clave feed air | Inaccurate reading | Tapping blocked | Y | Malfunction of air control loop | PM | Insp tapping | 104W | Maint | High pressure in clave. LOPA 25.09, 25.10
RV01 | Control loop | CL 02776 | FV02776 | Flow valve | VA | Valves | SPO | Spurious operation | Mechanical failure | Sticking | Control vessel feed air | Erratic control | Sticky movement | N | Malfunction of air control loop | PM | Stroke check | 104W | Maint
RV01 | Control loop | CL 02776 | FV02776 | Flow valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | Control vessel feed air | Passing | Wear | Y | Potential over pressure of vessel | PM | OSR | 208W | Maint
RV01 | Control loop | CL 02764 | XV02764 | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel discharge block 1 bottom Jamesbury | Passing | Wear | Y | Unable to control vessel pressure | PM | Replace | 4 days | Maint
RV01 | Control loop | CL 02764 | XV02764 | Actuated on/off valve | VA | Valves | FTO | Failure to open on demand | Material failure | Wear | vessel discharge block 1 bottom Jamesbury | Stuck closed | Nickel plating within ball and seat. | Y | Potential over pressure of vessel | Spare | Rotable spare | As needed | Maint
RV01 | Control loop | CL 02764 | XV02764 | Actuated on/off valve | VA | Valves | FTF | failure to function on demand | Mechanical failure | Sticking | vessel discharge block 1 bottom Jamesbury | Proxy not switching | Knocked/ ingress | N | Unable to control vessel pressure | PM | Align & Stroke | TAR | Operations
RV01 | Control loop | CL 02764 | XV02764 | Actuated on/off valve | VA | Valves | FTF | failure to function on demand | Mechanical failure | Clearance/ alignment failure | vessel discharge block 1 bottom Jamesbury | Proxy not switching | Misalignment | N | Unable to control vessel pressure
ACX1 |  | Loop 02764 | ZSO02764 | Position switch open |  |  | PLU |  | External influence | Blockage/ plugged | Clave discharge block 1 bottom Jamesbury | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
ACX1 |  | Loop 02764 | ZSC02764 | Position switch closed |  |  | PLU |  | External influence | Blockage/ plugged | Clave discharge block 1 bottom Jamesbury | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
RV01 | Control loop | CL 02765 | XV02765 | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel discharge block 2 top Jamesbury | Passing | Wear | Y | Unable to control vessel pressure | PM | Replace | 4 days | Maint
RV01 | Control loop | CL 02765 | XV02765 | Actuated on/off valve | VA | Valves | FTO | Failure to open on demand | Mechanical failure | Sticking | vessel discharge block 2 top Jamesbury | Stuck closed | Nickel plating within ball and seat. | Y | Potential over pressure of vessel | Spare | Rotable spare | As needed | Maint
ACX1 |  | Loop 02765 | XV02765 | Actuated on/off valve |  |  | PLU |  | External influence | Blockage/ plugged | Clave discharge block 2 top Jamesbury | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
RV01 | Control loop | CL 02765 | XV02765 | Actuated on/off valve | VA | Valves | FTF | failure to function on demand | Mechanical failure | Clearance/ alignment failure | vessel discharge block 2 top Jamesbury | Proxy not switching | Misalignment | N | Unable to control vessel pressure
ACX1 |  | Loop 02765 | ZSO02765 | Position switch open |  |  | PLU |  | External influence | Blockage/ plugged | Clave discharge block 2 top Jamesbury | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
ACX1 |  | Loop 02765 | ZSC02765 | Position switch closed |  |  | PLU |  | External influence | Blockage/ plugged | Clave discharge block 2 top Jamesbury | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
RV01 | Control loop | CL 02848H | XV02848H | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel discharge telltale to check if 2 blocks are blocking | Passing | Wear | Y | Unable to control vessel pressure | PM | Replace | 4 days | Maint
RV01 | Control loop | CL 02848H | XV02848H | Actuated on/off valve | VA | Valves | INL | Internal leakage | Mechanical failure | Sticking | vessel discharge telltale to check if 2 blocks are blocking | Stuck closed | Nickel plating within ball and seat. | Y | Potential over pressure of vessel | Spare | Rotable spare | As needed | Maint
ACX1 |  | Loop 02848H | XV02848H | Actuated on/off valve |  |  | PLU |  | External influence | Blockage/ plugged | Clave discharge telltale to check if 2 blocks are blocking | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
RV01 | Control loop | CL 02848H | XV02848H | Actuated on/off valve | VA | Valves | FTO | Failure to open on demand | Mechanical failure | Clearance/ alignment failure | vessel discharge telltale to check if 2 blocks are blocking | Proxy not switching | Misalignment | N | Unable to control vessel pressure
ACX1 |  | Loop 02848H | ZSC02848H | Position switch closed |  |  | PLU |  | External influence | Blockage/ plugged | Clave discharge telltale to check if 2 blocks are blocking | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
RV01 | Control loop | CL 02826 | XV02826H | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel feed block | Passing | Wear | Y | Feed leaking | PM | OSR | 52W | Maint
RV01 | Control loop | CL 02826 | XV02826H | Actuated on/off valve | VA | Valves | INL | Internal leakage | Material failure | Wear | vessel feed block | Passing | Wear | Y | Feed leaking | Spare | Rotable spare | As needed | Maint
ACX1 |  | Loop 02826 | ZSO02826 | Position switch open |  |  | PLU |  | External influence | Blockage/ plugged | Clave feed block | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
ACX1 |  | Loop 02826 | ZSC02826 | Position switch closed |  |  | PLU |  | External influence | Blockage/ plugged | Clave feed block | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
RV01 | Control loop | CL 02140H | XV02140H | Actuated on/off valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | HP Nitrogen to A Redn vessel block valve | Passing | Wear | Y | N2 leaking into vessel | PM | OSR | 208W | Maint
RV01 | Control loop | CL 02140H | XV02140H | Actuated on/off valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | HP Nitrogen to A Redn vessel block valve | Passing | Wear | Y | N2 leaking into vessel | Spare | Rotable spare
ACX1 |  | Loop 02140H | ZSO02140H | Position switch open |  |  | PLU |  | External influence | Blockage/ plugged | HP Nitrogen to A Redn clave block valve | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
ACX1 |  | Loop 02140H | ZSC02140H | Position switch closed |  |  | PLU |  | External influence | Blockage/ plugged | HP Nitrogen to A Redn clave block valve | Proxy not switching | Knocked/ ingress | N | Unable to control clave pressure | PM | Align & Stroke | TAR | Operations | Stops sequence if in the middle of cycle. High count of failures.
ACX1 |  | Loop 02800H | FIT02800H | Flow indicating transmitter |  |  |  |  | Instrument failure | Faulty signal | Control clave feed | Inaccurate reading | Inherent | Y | Erratic control of clave feed | PM | Internal inspection of the flow meter | 208W | Maint | Rely on high level switch. Over filling of the clave. LOPA 25.18
ACX1 |  | Loop 02800H | FIT02800H | Flow indicating transmitter |  |  | AIR |  | External influence | Blockage/ plugged | Control clave feed | Inaccurate reading | Buildup/ sheddar damage | Y | Inaccurate flow reading | PM | Internal inspection of the flow meter | 208W | Maint | Rely on high level switch. Over filling of the clave. LOPA 25.19
RV01 | Control loop | CL 02800H | FIT02800H | Flow indicating transmitter | CL | Control logic units | AIR | Abnormal Instrument Air | Instrument failure | Control failure | Control vessel feed | Leak to external | Sheddar seal deterioration | N | Feed leaking into vessel | PM | Inspection of the flow meter and seals | 208W | Maint
RV01 | Control loop | CL 02800H | FV02800H | Flow valve | VA | Valves | ELP | External leakage process medium | Mechanical failure | Leakage | Control vessel feed | Leak to external | Sheddar seal deterioration | N | Feed leaking into vessel | Spare | Rotable spare | As needed | Maint
RV01 | Control loop | CL 02800H | FV02800H | Flow valve | VA | Valves | SPO | Spurious operation | Mechanical failure | Sticking | Control vessel feed | Erratic control | Sticky movement | Y | Erratic control of vessel feed | PM | Stroke check | 104W | Maint
RV01 | Control loop | CL 02800H | FV02800H | Flow valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | Control vessel feed | Passing | Wear | Y | Feed leaking when valve is closed | PM | OSR | 52W | Maint
RV01 | Control loop | CL 02800H | FV02800H | Flow valve | VA | Valves | INL | Internal leakage | Mechanical failure | Clearance/ alignment failure | Control vessel feed | Passing | Wear | Y | Feed leaking when valve is closed | Spare | Rotable spare | As needed | Maint
Note on L1: Administrator: Functional purpose What is the primary/secondary purpose of this equipment/system? What it is supposed to do? What is the standard of performance? Any acceptance criteria/tolerable limits? Any HSEC/legal/reputation related impacts?

## ISO14224_Check
Excel Row | AssetID | FunctionalLocation | Component_ID | Component information | FMEA Equipment Class Code | FMEA Equipment Class Description | Checked/Infered Class | Class Source | FMEA FM Code | FMEA FM Description | Company Failure Mode | Company Failure Mechanism | Compliance Issue | Suggested Action
2 | ACX1 | Loop 02767 | LSH02767 | Radiation level sensor |  |  | Input devices | inferred from component information |  |  | Not switching | Misalignment | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
3 | ACX1 | Loop 02767 | LSH02767 | Radiation level sensor |  |  | Input devices | inferred from component information |  |  | Not switching | Misalignment | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
6 | ACX1 | Loop 02766 | TE02766 | Temperature sensor |  |  | Input devices | inferred from component information |  |  | Inaccurate reading | Inherent | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
7 | RV01 | CL 02766 | TIT02766 | Temperature indicating transmitter | CL | Control logic units | Control logic units | explicit | AIR | Abnormal Instrument Air | Inaccurate reading | Inherent | FM code is valid in ISO 14224 but not shown for equipment class 'Control logic units' in Table B.9 | AIR is not shown for control logic units in Table B.9; check the equipment class or choose an allowed CL failure mode.
10 | ACX1 | Loop 02773 | PIT02773 | Pressure indicating transmitter |  |  | Input devices | inferred from component information |  |  | Inaccurate reading | Inherent | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
11 | ACX1 | Loop 02773 | PIT02773 | Pressure indicating transmitter |  |  | Input devices | inferred from component information | PLU |  | Tapping blocked | Process conditions | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
12 | ACX1 | Loop 02773 | PIT02773 | Pressure indicating transmitter |  |  | Input devices | inferred from component information | PLU |  | Tapping blocked | Process conditions | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
13 | ACX1 | Loop 02774 | PIT02774 | Pressure indicating transmitter |  |  | Input devices | inferred from component information | AIR |  | Inaccurate reading | Inherent | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | AIR is shown for valves in Table B.9, not input devices; consider HIO, LOO, ERO, NOO or another allowed input-device FM code.
14 | ACX1 | Loop 02774 | PIT02774 | Pressure indicating transmitter |  |  | Input devices | inferred from component information | PLO |  | Tapping blocked | Process conditions | FM code is not in ISO 14224 Annex B failure mode code list | Possible typo for PLU (Plugged/choked), but only use PLU where the equipment-class table allows it.
15 | ACX1 | Loop 02774 | PIT02774 | Pressure indicating transmitter |  |  | Input devices | inferred from component information | PLO |  | Tapping blocked | Process conditions | FM code is not in ISO 14224 Annex B failure mode code list | Possible typo for PLU (Plugged/choked), but only use PLU where the equipment-class table allows it.
20 | ACX1 | Loop 02774 | ZI02774-3 | Position indicator |  |  | Input devices | inferred from component information |  |  | Passing | Wear | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
21 | ACX1 | Loop 02774 | ZSC02774-3 | Position switch closed |  |  | Input devices | inferred from component information |  |  | Passing | Wear | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
26 | ACX1 | Loop 02778 | ZSO02778 | Position switch open |  |  | Input devices | inferred from component information |  |  | Passing | Wear | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
27 | ACX1 | Loop 02778 | ZSC02778 | Position switch closed |  |  | Input devices | inferred from component information |  |  | Passing | Wear | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
30 | ACX1 | Loop 02777 | ZSO02777 | Actuated on/off valve |  |  | Input devices | inferred from component ID |  |  | Passing | Wear | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
31 | ACX1 | Loop 02777 | ZSC02777 | Actuated on/off valve |  |  | Input devices | inferred from component ID |  |  | Passing | Wear | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
32 | ACX1 | Loop 02776 | FIT02776 | Flow indicating transmitter |  |  | Input devices | inferred from component information |  |  | Inaccurate reading | Inherent | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
33 | ACX1 | Loop 02776 | FIT02776 | Flow indicating transmitter |  |  | Input devices | inferred from component information | PLU |  | Inaccurate reading | Tapping blocked | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
38 | RV01 | CL 02764 | XV02764 | Actuated on/off valve | VA | Valves | Valves | explicit | FTF | failure to function on demand | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Valves' in Table B.9 | For valves, use FTO, FTC, DOP, SPO, PLU, INL, LCP, etc. as applicable; FTF is not shown for valves in Table B.9.
39 | RV01 | CL 02764 | XV02764 | Actuated on/off valve | VA | Valves | Valves | explicit | FTF | failure to function on demand | Proxy not switching | Misalignment | FM code is valid in ISO 14224 but not shown for equipment class 'Valves' in Table B.9 | For valves, use FTO, FTC, DOP, SPO, PLU, INL, LCP, etc. as applicable; FTF is not shown for valves in Table B.9.
40 | ACX1 | Loop 02764 | ZSO02764 | Position switch open |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
41 | ACX1 | Loop 02764 | ZSC02764 | Position switch closed |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
45 | RV01 | CL 02765 | XV02765 | Actuated on/off valve | VA | Valves | Valves | explicit | FTF | failure to function on demand | Proxy not switching | Misalignment | FM code is valid in ISO 14224 but not shown for equipment class 'Valves' in Table B.9 | For valves, use FTO, FTC, DOP, SPO, PLU, INL, LCP, etc. as applicable; FTF is not shown for valves in Table B.9.
46 | ACX1 | Loop 02765 | ZSO02765 | Position switch open |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
47 | ACX1 | Loop 02765 | ZSC02765 | Position switch closed |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
52 | ACX1 | Loop 02848H | ZSC02848H | Position switch closed |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
55 | ACX1 | Loop 02826 | ZSO02826 | Position switch open |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
56 | ACX1 | Loop 02826 | ZSC02826 | Position switch closed |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
59 | ACX1 | Loop 02140H | ZSO02140H | Position switch open |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
60 | ACX1 | Loop 02140H | ZSC02140H | Position switch closed |  |  | Input devices | inferred from component information | PLU |  | Proxy not switching | Knocked/ ingress | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | For sensors/transmitters/switches, blocked tapping/ingress is better represented as mechanism/cause; use an allowed input-device FM such as FTF, HIO, LOO, ERO, NOO, etc. as applicable.
61 | ACX1 | Loop 02800H | FIT02800H | Flow indicating transmitter |  |  | Input devices | inferred from component information |  |  | Inaccurate reading | Inherent | Missing ISO 14224 failure mode code | Select the closest ISO 14224 FM code from the relevant equipment-class table.
62 | ACX1 | Loop 02800H | FIT02800H | Flow indicating transmitter |  |  | Input devices | inferred from component information | AIR |  | Inaccurate reading | Buildup/ sheddar damage | FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | AIR is shown for valves in Table B.9, not input devices; consider HIO, LOO, ERO, NOO or another allowed input-device FM code.
63 | RV01 | CL 02800H | FIT02800H | Flow indicating transmitter | CL | Control logic units | Control logic units | explicit | AIR | Abnormal Instrument Air | Leak to external | Sheddar seal deterioration | FM code is valid in ISO 14224 but not shown for equipment class 'Control logic units' in Table B.9 | AIR is not shown for control logic units in Table B.9; check the equipment class or choose an allowed CL failure mode.

## ISO14224_Summary
ISO 14224 FMEA code compliance summary
Total FMEA rows checked | 66
Rows with missing/non-compliant/unsupported code | 33
Issue type | Count | Basis | Notes
FM code is not in ISO 14224 Annex B failure mode code list | 2 | ISO 14224 Annex B Table B.9 and Tables B.6-B.12 code list
FM code is valid in ISO 14224 but not shown for equipment class 'Control logic units' in Table B.9 | 2 | ISO 14224 Annex B Table B.9 and Tables B.6-B.12 code list
FM code is valid in ISO 14224 but not shown for equipment class 'Input devices' in Table B.9 | 14 | ISO 14224 Annex B Table B.9 and Tables B.6-B.12 code list
FM code is valid in ISO 14224 but not shown for equipment class 'Valves' in Table B.9 | 3 | ISO 14224 Annex B Table B.9 and Tables B.6-B.12 code list
Missing ISO 14224 failure mode code | 12 | ISO 14224 Annex B Table B.9 and Tables B.6-B.12 code list
Important interpretation
Rows with blank FM code were treated as missing ISO 14224 coding.
Rows with blank equipment class were class-inferred from Component_ID / Component information where possible.
PLU used on transmitters/switches was flagged because Table B.9 shows PLU for valves, not input devices.
AIR used on input devices/control logic units was flagged because Table B.9 shows AIR for valves only.
FTF used on valves was flagged because Table B.9 uses FTO/FTC/DOP etc. for valves rather than FTF.
https://chatgpt.com/g/g-p-6a016955ce408191bd23279bdf8a1602-fm-code-check/c/6a017122-1198-83ec-aec8-2a182c83d994

## ISO14224_Ref_B9
Equipment class | Allowed FM codes from ISO 14224 Table B.9 | Source table | Notes
Valves | AIR, DOP, ELP, ELU, FTC, FTO, HIO, INL, LCP, LOO, OTH, PLU, SER, SPO, STD, UNK | Table B.9 | Safety and control equipment
Control logic units | ERO, FTF, HIO, LOO, OTH, SER, SPO, UNK | Table B.9 | Safety and control equipment
Input devices | ELP, ELU, ERO, FTF, HIO, LOO, NOO, OTH, SER, SPO, UNK | Table B.9 | Safety and control equipment
Fire detectors | ERO, FTF, HIO, LOO, NOO, OTH, SER, SHH, SLL, SPO, UNK | Table B.9 | Safety and control equipment
Gas detectors | HIO, LOO, NOO, OTH, SER, SHH, SLL, SPO, UNK, VLO | Table B.9 | Safety and control equipment